UPS Communications Protocol

SMES

202205

Content

1 Description	3

1.1 Scope	3

1.2 Reference document	3

1.3 Glossary – Abbreviations – Notations	3

2 Hardware Description	3

3 Communication Instructions	4

3.1 Inquiry Command	4

3.1.1 Q1<cr>: Status Inquiry 1	4

3.1.2 Q4<cr>: Status Inquiry 4	5

3.1.3 Q6<cr>: Status Inquiry Instruction Q6	6

3.1.4 QFC<cr>: Fault Status Inquiry	8

3.1.5 QP<cr>: Control parameters inquiry	11

3.1.6 VS?<cr>: Output voltage inquiry command	12

3.1.7 BM?<cr>: query/set entity bypass en-disable; （only for 1-3K UPS）	12

3.1.8 BO?<cr>: query/set auto bypass en-disable; （only for 1-3K UPS）	12

3.1.9 WC query out power status of the UPS (for 1-3K UPS only)	12

3.1.10 SF?<cr>:  query line Frequency range.	12

3.1.11 RT Query setup and type information about the UPS	13

3.2 Control Command	13

3.2.1 T<cr>: 10 seconds test command	13

3.2.2 TL<cr>: Test until battery low command	13

3.2.3 T<n><cr>: Test for specified time command	14

3.2.4 S<n><cr>: Shutdown command	14

3.2.5 S<n>R<m><cr>: Shutdown and restore command	14

3.2.6 C<cr>: Cancel shutdown command	14

3.2.7 CT<cr>: Cancel test command	14

3.2.8 ZON<cr>: Remote turn on UPS command	14

3.2.9 ZOFF<cr>: Remote turn off UPS command	15

3.3 Setting parameters Command	15

3.3.1 PE<n>/PD<n>: <cr>:  enable or disable parameter that follow	15

3.3.2 PF<cr>: Set control parameter to default value  （for 1-3K UPS only）	15

3.3.3 VS<rrr><cr>: Set Output voltage inquiry command	15

3.3.4 BV?<cr>: Query /set bypass voltage rang	15

3.3.5 BV<ppp qqq> <cr>:  Set bypass voltage rang	16

3.3.6 FS?<cr>: Query output frequency	16

3.3.7 FS<nn><cr>: Set output frequency	16

Description

Scope

This document specifies the RS232 communication protocol used in 1-20K UPS.

1~3K UPS

6-10K UPS

10-20K 3/1 UPS

Reference document

Glossary – Abbreviations – Notations

ECO Mode: High Efficiency Mode, same with HE mode.

CVCF: Fix Frequency Converter Mode.

Hardware Description

BAUD RATE...............: 2400 bps

DATA LENGTH..........: 8 bits

STOP BIT.....................: 1 bit

PARITY........................: NONE

Cabling:

COMPUTER                  UPS

===================================

(9 pins female D-type Connector)

Communication Instructions

Inquiry Command

Q1<cr>: Status Inquiry 1

Computer: Q1<CR>

UPS acknowledge: (MMM.M NNN.N PPP.P QQQ RR.R S.SS TT.T b7b6b5b4b3b2b1b0<cr>

The binary code is modified to 8 bytes ASCII code for avoiding the binary code confused with ASCII control code. Between each data stream add one space for the data separation.

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| B | MMM.M | I/P voltage | M is an integer number ranging from 0 to 9. The units is V. |
| c | NNN.N | I/P fault voltage | N is an integer number ranging from 0 to 9. The units is V. Its purpose is to identify a short duration utility fail which cause ON line UPS to go to Battery mode. If this occurs input voltage will appear normal at query prior to fail and will still appear normal at next query. The I/P fault voltage will hold utility fail voltage till next query. After query, the I/P voltage will be same as I/P voltage until next utility fail occurs. |
| d | PPP.P | O/P voltage | P is an integer number ranging from 0 to 9. The units is V. |
| e | QQQ | O/P load | QQQ is the maximum of W% or VA%. VA% is a percent of appearance power VA. W% is a percent of real power. |
| f | RR.R | I/P frequency | R is an integer number ranging from 0 to 9.The units is Hz. |
| g | SS.S or S.SS | Cell Volt of Battery | S is an integer number ranging from 0 to 9. For on-line units battery voltage/cell is provided in the form S.SS .For standby units actual battery voltage is provided in the form SS.S .UPS type in UPS status will determine which reading was obtained. |
| h | TT.T | Temperature | T is an integer number ranging from 0 to 9. The unit is degree of centigrade. |
| i | B7 B6 B5 B4 B3B2 B1 B0 | UPS status Where <bn> is a binary number "0" or "1". | Bit7 1 : Utility Fail ( Immediate ) Bit6 1 : Battery Low Bit5 1 : Bypass/Boost Active Bit4 1 : UPS Failed Bit3 1 : UPS Type is Standby (0 is On-line) Bit2 1 : Test in Progress Bit1 1 : Shutdown Active Bit0 0 : Bat mode silence |

Example:

Computer:

Q1<cr>

UPS:

(208.4 140.0 220.6 034 49.9 2.05 55.0 00110000<cr>

Means:

I/P voltage is 208.4V.

I/P fault voltage is 140.0V.

O/P voltage is 220.6V.

O/P load level is 34% of rated load.

I/P frequency is 49.9 Hz.

Battery voltage is 2.05V/cell(6cell per pcs of Lead-acid Battery).

Temperature is 55.0 degrees of centigrade.

UPS type is on-line, UPS failed, Bypass active, and Shutdown not active.

Q4<cr>: Status Inquiry 4

Computer：Q4<cr>

UPS:  (MMM.M HHH.H LLL.L NNN.N PPP.P QQQ DDD RR.R KKK VVV SSS.S TT.T XXXXXXXX<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | MMM.M | Input voltage | M is an Integer number 0 to 9. The units is V. |
| c | HHH.H | Input maximum voltage | H is an Integer number 0 to 9. The units is V. |
| d | LLL.L | Input minimum voltage | L is an Integer number 0 to 9. The units is V. |
| e | NNN.N | Input fault voltage | N is an Integer number ranging from 0 to 9. The units is V. |
| f | PPP.P | Output voltage | P is an Integer number ranging from 0 to 9. The units is V. |
| g | QQQ | Output current percent | QQQ is a percent of maximum current, not an absolute value |
| h | DDD | Output load percentage | For On-line UPS: LLL is Maximum of W% or VA%. VA% is a percent of maximum VA. W% is a percent of maximum real power. |
| i | RR.R | Input frequency | R is an integer ranging from 0 to 9. The units is Hz. |
| j | KKK | Positive BUS voltage | K is an Integer ranging from 0 to 9. The units is V. |
| k | VVV | Negative BUS voltage | V is an Integer ranging from 0 to 9. The units is V. |
| l | SSS.S | Battery voltage | S is an Integer ranging from 0 to 9. The units is V. |
| l | TT.T | Temperature | T is an integer ranging from 0 to 9. The units is °C |
| m | XXXXXXXX | Ups status | X :represents UPS status, may present more than one letter at the same time according to real status A: Line Loss B: Battery Low C: Bypass/Boost Active D: UPS Failed E: Test in Progress F: Shutdown Active G: SITE fault H: EPROM fail I: Test passed – Result: OK J: Test passed – Result: Failed K: Test not Possible or Inhibited L: Test Status Unknown M: UPS normal mode N: UPS 110% overload O~Z are reserved for the future use. |

Example:

Computer: Q4<cr>

UPS:(220.2 250.5 200.0 136.0 220.2 100 100 50.0 370 375 41.0 45.0 LM<cr>

Means: I/P voltage is 220.2V.

Maximum I/P voltage is 250.5V

Minimum I/P voltage is 200.0V

I/P fault voltage is 136.0V.

O/P voltage is 220.2V.

O/P current is 100%

O/P load 100%

I/P frequency is 50.0 HZ.

Positive BUS voltage is 370V

Negative BUS voltage is 375V

Battery voltage is 41.0V.

Temperature is 45.0 degrees of centigrade.

Test Status Unknown and UPS status is line mode.

Q6<cr>: Status Inquiry Instruction Q6

Computer：Q6<cr>

UPS: (MMM.M ---.- ---.- NN.N PPP.P ---.- ---.- RR.R QQQ --- --- VVV.V---.-

TT.T ttttt CCC KB ffffffff wwwwwwww YO<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | MMM.M | Input voltage | M is an Integer number 0 to 9. The units is V. |
| c | ---.- | Reserved |  |
| d | ---.- | Reserved |  |
| e | NN.N | Input frequency | N is an Integer number ranging from 0 to 9. The units is Hz. |
| f | PPP.P | Output voltage | P is an Integer number ranging from 0 to 9. The units is V. |
| g | ---.- | Reserved |  |
| h | ---.- | Reserved | ---.- |
| i | RR.R | Inverter output frequency | R is an integer ranging from 0 to 9. The units is Hz. |
| j | QQQ | Output current percentage of rated current | The units is % |
| k | --- | Reserved |  |
| l | --- | Reserved |  |
| m | VVV.V | Bat voltage VVV.V | S is an integer ranging from 0 to 9. The units is V |
| n | ---.- | Reserved | ---.- |
| o | TT.T | Temperature | T is an integer ranging from 0 to 9. The units is °C |
| p | ttttt | Reserved | Reserved |
| q | CCC | Rough Estimated Battery level | % |
| r | K | UPS mode | UPS MODE K: 0 Power-on mode 1 Standby mode 2 Bypass mode 3 Line mode 4 Bat mode 5 Battery Test mode 6 Fault mode 7 Converter mode 8 ECO mode 9 Shutdown Mode |
| s | B | battery test status | battery test status: 0 idle 1 processing 2 result : no failure 3 result : failure / warning 4 Not possible or inhibited 5 Test cancel 6 Reserved 7 Other values |
| t | ffffffff | Fault code |  |
| u | wwwwwwww | warning code |  |
| v | YO | UPS type | Single phase input Single Phase Output:11, Three phases input Single Phase Output: 31 |

Example：

Send: →◇Q6

Receive (235.8 000.0 000.0 50.0 237.4 ---.- ---.- 50.1 000 --- --- 218.5 ---.- 26.3 99999 100 20 00000000 00000000 11

Meaning:

Input voltage：235.8V

Input frequency：50.0Hz

output voltage：237.4V

Inverter output frequency： 0.0HZ

Battery Voltage：218.5V

Ups converter temperature:  26.3 degree

estimated battery percentage: 100%

UPS operating mode：  20   bypass mode， No

fault code：00000000   NO FAULT CODE

warning code：00000000   NO ALARM CODE

UPS type：11   Single phase input , single phase output

QFC<cr>: Fault Status Inquiry

Computer: QFC<cr>

UPS: (KK MM XXXXX XXXXX XXXXX PPP FF.F OOO EE.E LLL CCC PPP NNN PPPP NNNN BBB.B TTT TTT SSSSS CCCCC PPPPP<cr>

(a) Start byte: (

(b) Fault kind: KK

KK is 2 bytes of ASCII code, define as following:

(c) UPS operating mode when fault occurs: MM

Meaning:	Line mode		0

Battery Mode		1

ECO Mode		2

Bypass Mode	3

Standby Mode	4

Fault Mode	5

Power On Mode	6

Shutdown Mode	7

(d) External warning code 1: XXXXX

Meaning:

| Line loss | 0x0008 |
| --- | --- |
| LN reverse | 0x0040 |
| Bypass loss | 0x0080 |
| Battery note connected | 0x0200 |
| Battery low | 0x0400 |
| Battery over charge | 0x0800 |
| Over load warning | 0x4000 |
| Fan fail | 0x8000 |

(e External warning code 2:XXXXX

| Charger failure | 0x0002 |
| --- | --- |

(f) Internal warning code 1: XXXXX(00000)

(g) I/P voltage before fault: PPP

P is an integer number ranging from 0 to 9. The unit is Volt.

(h) I/P frequency before fault: FF.F

F is an integer number ranging from 0 to 9. The unit is HZ.

(i) Inverter O/P voltage before fault: OOO

O is an integer number ranging from 0 to 9. The unit is Volt.

(j) Inverter O/P frequency before fault: EE.E

E is an integer number ranging from 0 to 9. The unit is HZ.

(k) O/P load percentage before fault: LLL

LLL is the maximum of W% or VA%.

VA% is a percent of maximum VA.

W% is a percent of maximum real power.

(l) O/P current percentage before fault: CCC

CCC is a percent of maximum current.

(m Positive Bus voltage before fault: PPP

P is an integer number ranging from 0 to 9. The unit is volt.

(n) Negative Bus voltage before fault: NNN

N is an integer number ranging from 0 to 9. The unit is volt.

(o)  Positive BUS voltage sampling result before fault: PPPP

P is an integer number ranging from 0 to 9.

(p)  Negative BUS voltage sampling result before fault: NNNN

N is an integer number ranging from 0 to 9.

(q) Battery voltage before fault: BBB.B

B is an integer number ranging from 0 to 9. The unit is volt

(r) Temperature before fault: TTT

T is an integer number ranging from 0 to 9. The unit is degree of centigrade.

(s) Heat-sink temperature before fault: TTT

T is an integer number ranging from 0 to 9. The unit is degree of centigrade.

(t) System statue before fault：SSSSS

(u) Converter statue before fault：CCCCC

Meaning:		Converter stop working	0

Converter working in Line mode 	1

Converter working in battery mode	2

(v) phase-lock status before fault occur：PPPPP

Meaning:		phase-lock success 1

phase-lock not ready	2

Example:

Computer: QFC<cr>

UPS: (02 00 00000 00000 00000 223 50.0 220 50.0 110 109 455 309 1566 1096 012.8 029 029 				00015 00001 00001<cr>

Represent:

(b) Fault code: 02  BUS Over voltage protection

- UPS operating mode before fault: Line mode

(d) external warning code1: 00000

(e) external warning code 2: 00000

(f) Internal warning code: 00000

(g) Line voltage before fault: 223V

(h) Line Frequency before fault: 50.0HZ

(i) Output voltage before fault:220V

(j) Output frequency before fault: 50.0HZ

(k) Output load level before fault: 110%

(l) Output current level before fault: 109%

(m)Positive BUS voltage before fault: 455V

(n)Negative BUS voltage before fault: 309V

(o) Positive BUS voltage sampling result before fault: 1566

(p) Negative BUS voltage sampling result before fault:1096

(q) Battery voltage before fault: 12.8V

(r) Heatsink1 temperature: 29℃

(s) Heatsink2 temperature: 29℃

(t) System statue before fault：Input relay close ,PFC working , Inverter relay close, Inverter working.

(u) input stage converter working statue：On line mode

(v)Phase lock status：Phase-lock success

QP<cr>: Control parameters inquiry

Computer: QP<cr>

UPS: (MM.M NN.N PPP QQQ ExxxDxxx<cr>

Example:

Computer: QP<cr>

UPS: (46.0 54.0 80 264 EpkraDbco<cr>

Means:  Low threshold frequency on bypass is 46.0Hz.

High threshold frequency is on bypass is 54.0Hz.

Low voltage range on bypass is 80V.

High voltage range on bypass is 264V.

Enable bypass audible warning.

Disable battery mode audible warning.

Enable key control bypass audible warning.

Disable key control battery mode audible warning.

Enable auto-reboot.

Disable bypass when UPS off.

Enable audible alarm.

Although the “P” command set one or several parameters before, the “QP” command can inquiry all parameters

Example:

Computer: PG59.9<cr>

UPS: set high threshold  frequency on bypass to 59.9Hz

Computer: QP<cr>

UPS: (46.0 59.9 80 264 EpkraDbco<cr>

VS?<cr>: Output voltage inquiry command

Computer: VS?<cr>

UPS: (V200/208/220/230/240<cr>

BM?<cr>: query/set entity bypass en-disable; （only for 1-3K UPS）

computer: BM?<cr>

UPS: x<cr>

X:  0  entity bypass disable

1   entity bypass enable

Computer: BM<n><cr>

UPS: ACK

X:  0  SET entity bypass disable

1  SET entity bypass enable

BO?<cr>: query/set auto bypass en-disable; （only for 1-3K UPS）

computer: BO?<cr>

UPS: x<cr>

X:  0  auto bypass disable

1   auto bypass enable

Computer: BO<n><cr>

UPS: <n>

X:  0  SET auto bypass disable

1  SET auto bypass enable

WC query out power status of the UPS (for 1-3K UPS only)

Computer: WC

UPS:(PPPP SSSS<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | PPPP | UPS op active power W | P is an Integer number 0 to 9. Unit: W |
| c | SSSS | UPS op total power VA | S is an Integer number 0 to 9. Unit: VA |

SF?<cr>:  query line Frequency range.

Computer: SF? query line Frequency range set

UPS: (HH.H LL.L<cr>

| Data | Description | Notes |
| --- | --- | --- |
| ( | Start byte |  |
| HH.H | Line frequency upper limit | H is an Integer number 0 to 9. Unit: Hz |
| LL.L | Line frequency lower limit | L is an Integer number 0 to 9. Unit: Hz |

RT Query setup and type information about the UPS

Computer: RT

UPS:(VV.VV PP.PP TTTTTTTTTTTTTTTTTTTTTTTTTTTTTT S/S P/P MMM FF.FF RRR BB.B NN WWWWW<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | VV.VV | UPS Firmware Version | V is an Integer number 0 to 9. unit-less |
| c | PP.PP | Protocol Number | P is an Integer number 0 to 9. unitless |
| d | TTTTTTTTTTTTTTTTTTTTTTTTTTTTTT | UPS Series and Model | T is an Integer number 0 to 9. unitless |
| e | S/S | Input Source Number/Output Source Number | S is an Integer number 0 to 9. unitless |
| f | P/P | Input Phase Number/Output Phase Number | P is an Integer number 0 to 9. unitless |
| g | MMM | Nominal Output Voltage | M is an Integer number 0 to 9. Unit: V |
| h | FF.FF | Nominal Output Frequency | F is an Integer number 0 to 9. Unit: Hz |
| i | RRR | Number of Battery Unit in Series | R is an Integer number 0 to 9. Unit: pcs |
| j | BB.B | Nominal Voltage per Battery Unit | B is an Integer number 0 to 9. Unit: V |
| k | NN | Reserve |  |
| l | WWWWW | Rated VA per UPS Module | 1000VA,2000VA,3000VA |

Control Command

T<cr>: 10 seconds test command

Computer: T<cr>

UPS: Test for 10 seconds and then return to utility.

If battery low occurs during testing, UPS will return to utility immediately.

TL<cr>: Test until battery low command

Computer: TL<cr>

UPS: Test until battery low and then return to utility.

This command is used to let the user to discharge the battery by setting the time to test, that is to say that the user should discharge the battery by periods, with this command the ups will do it by itself.

T<n><cr>: Test for specified time command

Computer: T<n><cr>

UPS: battery test for <n> minutes

<n> is an integer number form 01 to 99.

S<n><cr>: Shutdown command

Computer: S<n><cr>

UPS: Shut UPS output off in <n> minutes.

The UPS output will be off in <n> minutes, even if the utility is present.

But if the battery under occur before <n> minutes, the output is turned off immediately.

After UPS shut down, the controller of UPS monitors the utility. If the utility is there, the UPS will wait for 10 seconds and Connect the utility to output.

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 10.

For example: S.3<cr> --- shut out put off in ( .3) minutes

S<n>R<m><cr>: Shutdown and restore command

Computer: S<n>R<m><cr>

UPS: Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again.

The shut down sequence is the same as the previous command. When the <m> minutes expired, the utility do not restore, the UPS will wait until utility restore.

If UPS is in waiting shutdown status, the “C” command can let the shut down command canceled.

If UPS is in restore waiting status, the “C” command can let the UPS output turned on, but UPS must be hold off at least 10 seconds. (if utility is present)

<n> is a number ranging from .2, .3, ..., 01, 02, ..., to 99.

<m> is a number ranging from 0001 to 9999.

C<cr>: Cancel shutdown command

Computer: C<cr>

UPS: Cancel the SN<n><cr> and SN<n>R<m><cr> command.

If UPS is in waiting shutdown state, the shut down command is canceled.

If UPS is in waiting restore state, the UPS output is turned on, but UPS must be hold off at least 10 seconds. (If utility is present)

CT<cr>: Cancel test command

Computer: CT<cr>

UPS: Cancel all test activity and Connect  the utility to output immediately.

ZON<cr>: Remote turn on UPS command

Computer: ZON<cr>

UPS: (ZON <cr>

Means: Remote turn on UPS.

ZOFF<cr>: Remote turn off UPS command

Computer: ZOFF<cr>

UPS: (ZOFF <cr>

Means: Remote turn off UPS.

Setting parameters Command

PE<n>/PD<n>: <cr>:  enable or disable parameter that follow

| X | Control setting |
| --- | --- |
| P | Enable/disable bypass audible warning |
| B | Enable/disable battery mode audible warning |
| K | Enable/disable key control bypass audible warning. |
| C | Enable/disable key control battery mode audible warning. |
| R | Enable/disable auto-reboot. |
| O | Enable/disable bypass when UPS turn off. |
| A | Enable/disable audible alarm |

Example:

Computer: PEP<cr>

UPS:  Enable bypass audible warning.

Computer: PDA<cr>

UPS:  Disable audible alarm

PF<cr>: Set control parameter to default value  （for 1-3K UPS only）

Computer: PF<cr>

UPS: ACK<cr>

All UPS parameters set to default value.

Note: Only in bypass mode and standby mode.

VS<rrr><cr>: Set Output voltage inquiry command

Computer: VS<rrrr><cr>

UPS: (V200/208/220/230/240/250<cr>

BV?<cr>: Query /set bypass voltage rang

Computer: BV?<cr>

UPS: (MMM NNN<cr>

| Data | Description | Notes |
| --- | --- | --- |
| ( | Start byte |  |
| MMM | Upper limit of Bypass Voltage Range | M is an Integer number 0 to 9. Unit: V |
| NNN | Lower limit of Bypass Voltage Range | M is an Integer number 0 to 9. Unit: V |

BV<ppp qqq> <cr>:  Set bypass voltage rang

Computer: BVmmm nnn <cr>

UPS:ACK<cr>

| Data | Description | Notes |
| --- | --- | --- |
| ( | Start byte |  |
| ppp | bypass high voltage range will be (1+ppp/100)×nominal output voltage | p is an integer number from 0 to 9unit is ％ |
| qqq | Lower limit of Bypass Voltage Range will be :(1－qqq/100)×nominal output voltage | q is an integer number from 0 to 9unit is ％ |

For example the output nominal voltage is 220V,   and send command:

BV020 010<cr>

The bypass voltage upper limit will be:  220V*(1+20%)=264V

The bypass voltage lower limit will be:  220V*(1-10%)=198V

FS?<cr>: Query output frequency

Computer: FS?<cr>

UPS: ACK<cr>

| Data | Description | Notes |
| --- | --- | --- |
| ( | Start byte |  |
| NN | Output nominal frequency | 50Hz/ 60Hz. Unit: Hz |

FS<nn><cr>: Set output frequency

Computer: FS<kk><cr>

UPS: (kk<cr>

(note: if frequency auto adjust, UPS:(NN-00<cr>)

| Data | Description | Notes |
| --- | --- | --- |
| ( | Start byte |  |
| kk | Output nominal frequency | 00/50Hz/ 60Hz. Unit: Hz 00 means that the output frequency will auto adjust according to bypass(input) frequency. |

3.3.8 NB?<cr>:Query battery pcs (for 6-20K UPS only)

Computer:NB?<cr>

UPS:(NN<cr>

| Data | Description | Notes |
| --- | --- | --- |
| ( | Start byte |  |
| NN | Battery Pcs | 12/16/20 6K UPS 12/16 10K UPS 16/20 |

3.3.9 NB<kk><cr>:Set battery pcs  (for 6-20K UPS only)

Computer:NB<kk><cr>

UPS:ACK<cr>

| Data | Description | Notes |
| --- | --- | --- |
| ( | Start byte |  |
| kk | Battery pcs | 12/16/20 Only 6K UPS can set 12/16/20 10K/15K/20KS UPS can set 16/20 |